Mettler-Toledo AG,Process Analytics

FF Release Notes

Table of Contents

1	FF Device List	3

1.1	AMS,DeltaV list	3

1.2	Centum VP/PRM list	3

1.3	Others	3

2	Revision History	4

3	Installation for different host	4

3.1	AMS,DeltaV	4

3.2	Centum VP/PRM	4

3.3	HH375,HH475	4

3.4	Other	4

4	Know issues and limitations	4

4.1	General	4

4.2	AMS	5

4.2.1	Manufacturer independent problem	5

4.3	Centum VP/PRM	5

4.3.1	Manufacturer independent problem	5

4.4	NI-FBUS	5

# FF Device List

## AMS,DeltaV list

| Device Type | Dev Rev | DD Rev | CFF Rev | Min version | FF-Stack Rev | Transmitter Rev |
| --- | --- | --- | --- | --- | --- | --- |
| 0420 | 1 | 01 | 02 | 9.0 | 1.0.00 | 1.0.00 |

## Centum VP/PRM list

| Device Type | Dev Rev | DD Rev | CFF Rev | Min version | FF-Stack Rev | Transmitter Rev |
| --- | --- | --- | --- | --- | --- | --- |
| 0420 | 1 | 01 | 02 |  | 1.0.00 | 1.0.00 |

## Others

Tbd.

# Revision History

| Version | Description of changes |
| --- | --- |
| V1.0.00 2018/6/22 | First introduced to the package |

# Installation for different host

This chapter describes the standalone installation for different hosts.

For RPM software questions, contact the Yokogawa Support or refer to the Manual

For AMS software questions, contact the EMERSON Support or refer to the Manual

For further questions, contact the Mettler-Toledo Support.

## AMS,DeltaV

Close all of AMS application. Use the DD installation utility “Add Device Type”to install the DDs. During the installation warnings could appear in fact of already installed files which are used in different setups.For the detail steps about DD installation, refer to the AMS related installation manual delivered by Emerson.

## Centum VP/PRM

- Please close all applications before the installation

- Centum VP does not allow spaces in device tag. Please change default tag.

- During the installation warnings could appear in fact of already installed files which are used in different setups.

## HH375,HH475

- Min Required version is 3.6

## Other

- None.

# Know issues and limitations

## General

- We recommend performing an upload before the first commissioning. This ensures data consistency with the device and will prevent possible problems during the download.

- We recommend performing an device reset(power off and power on) after change sensor type or channel. Eg: change pH to O2 sensor.

## AMS,375,475

### Manufacturer independent problem

For further questions, contact the EMERSON Support or refer to the Manual.

## Centum VP/PRM

### Manufacturer independent problem

- Centum VP does not allow spaces in device tag. Please change default tag(“M400(G) FF“).

Valid characters are 0-9, A-Z, - and _.

For further questions, please contact the Yokogawa Support.

## NI-FBUS

- The NI-FBUS Configurator supports user methods. These methods are a sub-set of the FOUNDATIONTM Fieldbus Menus and Methods specification(reference NI-FUBS manual, see NI-FBUS manual).

Process calibration over NI-FBUS is not supported.